## Pre Bid Queries
Tender for Turnkey Supply Package for 5 nos. of 160 MVA, 220/33-33 kV Power Transformer at Radha Nesda, Gujarat, India
Tender No :SECI/C&P/OP/11/022/2025-26
Sl. No. | Tender Section | Page No. | Clause No | Description as per Tender Document | Queries | Category (Technical/Contractual) | Clarifications
1 | BID INFORMATION SHEET | 13 | (H) EARNEST MONEY DEPOSIT (EMD) | INR 1,50,00,000/- Crores (Indian Rupees One Crores and Fifty Lakhs only) | INR 1,50,00,000/- Crores (Indian Rupees One Crores and Fifty Lakhs only) We request for the waiver of submitting the EMD bank guarantee against this tender as per PGCIL tender. We will submit the bid security declaration signed by our authorized signatory. We are hopeful that board will definitely give due consideration and support us at this critical juncture. | Contractual | The terms and conditions of the tender document shall prevail.
2 | BID INFORMATION SHEET | 13 | (I) CONTRACT PERFORMANCE SECURITY | 10% of the Total Order Cost for a total period of 31 months. | 10% of the Total Order Cost for a total period of 31 months. We request honourable Tender Committee to reconsider the tender clause and requesting to reduce the performance security value to 3% of the contract value from 10%. | Contractual | The terms and conditions of the tender document shall prevail.
3 | BID INFORMATION SHEET | 13 | (K) ONLINE BID SUBMISSION DEADLINE | ONLINE BID SUBMISSION DEADLINE - 23.01.2026 up to 1400 HRS | ONLINE BID SUBMISSION DEADLINE - 23.01.2026 up to 1400 HRS We request you to kindly arrange to extend the due date for offer submission by Three (3) weeks, as we require additional time to prepare the detailed Techno-Commercial offer along with the necessary supporting documents. Furthermore, due to continuous holidays on account of the Sankranti, we require extra time to obtain the required Bank Guarantees towards Bid Security from our bankers. We sincerely request you to consider our request for due date extension and oblige. | Contractual | The bid submission will be extended to provide enough participation time to all the bidders post the Management approval and same will be reflected on ETS Portal and SECI's website.
4 | BID INFORMATION SHEET | 12 | (F) COMPLETION | Delivery completion16 months from the date LOA/PO | Delivery completion16 months from the date LOA/PO Kindly confirm the delivery requirement for each unit, and also provide the completion of service portion. | Technical | Delivery Schedule shall be as follows: Delivery of 1st Unit: 14 months from the Date of PO and balance quantity till 16 months
5 | SPECIAL PURCHASE CONDITIONS (SPC) | 142 | 13 | Schedule of Rates & Payments | for supply portion: we respectfully request the Tender Committee to consider enhancing the advance payment from the existing 10% to 20%, noting that precedence for an advance is already available with PGCIL in contracts. Further, we also request the Committee to kindly consider adoption of the payment terms from any one of the options mentioned below, which would facilitate smoother execution of the contract. Option-1 10% of the basic price of the order as interest free advance against submission of ABG. 10% of the basic price of the order against Drawing approval. Balance 80% of the basic price plus 100% taxes and duties shall be shall be paid through 30 days LC from the date of dispatch. the LC shall be established along with drawing approval. Option-2 Payment terms shall be as per PGCIL reference : Interest Free Advance (10%): Ten percent (10%) of the Ex-works price component of Main Equipment/Materials (including Mandatory Spares), shall be paid against submission of Advance Payment Security for 100% of the amount of Advance. Interest Free Engineering Advance (10%): Further advance of 10% (Ten Percent) of the Ex-works price component of Main Equipment/Materials (including Mandatory Spares) shall be paid against completion of all the CAT-1 o all the Engineering documents and submission of 100 Bank Guarantee/ Insurance Surety Bond in favour of the Employer for 100% (one hundred percent) of the amount of Interim Engineering Advance. Progressive Payment(70%): Seventy Percent (70%) of the Ex-Works price component of Main Equipment/Materials (including Mandatory Spares) shall be paid material Dispatch to site. Final Payment (10%): of the Ex-works price of Main Equipment/ materials (including Mandatory Spares) shall be paid on receipt and storage at site and on physical verification and furnishing of necessary certificate by Employer’s representative. | Contractual | The terms and conditions of the tender document shall prevail.
6 | SECTION - VII | 229 | 1.8 | Warranty | The transformer shall be warranted against all material/ manufacturing defects and workmanship for minimum of 5 (five) years from the last date of supply. The transformer shall be warranted against all material/ manufacturing defects and workmanship for the period of 5 (five) years from the date of commissioning (or) 5.5 months from the date of supply. on pro rata basis. | Technical | Terms and conditions shall prevail
7 | [A] - GENERAL | 28 | 11.5 | Price basis | Prices quoted by the Bidder, shall remain FIRM and Fixed and valid until completion of the Contract and will not be subject to variation on any account. As you are aware, at present there is volatility in the raw material prices of transformers. Hence, we propose changing the pricing from FIRM to variable price as per IEEMA so that we can offer competitive prices. | Contractual | Kindly refer Amendment 01 sheet.
8 | SECTION - VII | 216 | 3 | Scope of Supply | The scope of Supply includes Design, Engineering, Procurement, Manufacturing of Equipment and Materials, Routine Testing at works, Packing, Forwarding and Supply on FOR-Site basis (inclusive of comprehensive transit insurance till safe delivery) of 5 nos. of 160 MVA, 220 kV/33 – 33 kV Power Transformers and associated equipment for the 700 MW (AC) Solar PV Power Project. We understand our scope will be Supply includes Design, Engineering, Procurement, Manufacturing of Equipment and Materials, Routine Testing at works, Packing, Forwarding and Supply on FOR-Site basis. Unloading, Erection Testing and commissioning is not in our scope. kindly clarify, | Contractual | Kindly refer Amendment 01 sheet.
9 | SECTION - VII | 222 | 1.2 | Cooling Fans shall be of minimum IP66 protection. | Cooling Fans shall be of minimum IP66 protection. As per manufacturing standard, Cooling Fans IP65 protection will be provided. Kindly confirm the same | Technical | Please refer S. No. 5 of Amendment
10 | SECTION - VII | 223 | 1.5 | Painting | Shall be suitable for C-5 environment as per ISO 12944-5:2019. C5 paint applicable for tank (325microns) & radiator (245 microns + HDG). Accessories & valves are not considered for C5 paint. | Technical | Accessories and valves manufactured from inherently corrosion-resistant materials (e.g., gunmetal/bronze) need not be included in the C5 painting system. Any other exposed surfaces that are vulnerable to corrosion shall meet the specified environmental durability requirements. Please refer S. No. 6 Amendment.
11 | SECTION - VII | 225 | 1.6.10 | Scope of the cable | Scope shall also include communication cables between digital RTCC relays. Cables as required for parallel operation of OLTCs of all transformers (including existing transformers wherever required) from Digital RTCC relays shall be considered included in the scope of bidder. Cables required at site between transformer , control panel, Existing transformer are not in INDO TECH scope of supply. However cables for transformer to Marshalling box will be scope of supply. | Technical | Accepted.
12 |  |  |  |  | NA | Contractual | Query not clear.
13 |  |  | General points | CEA(Solar park pooling station) | 5.13. The transformer shall be designed with particular attention to the suppression of harmonic voltage, especially the third and fifth harmonics so as to minimise interference with communication circuits. Please note that transformer itself will not generate any harmonics nor it will filter out incoming harmonics. If any harmonics is coming from incoming side it will be passed on to outgoing side. | Technical | Terms and conditions of CEA specifications prevail
14 |  |  | General points | CEA(Solar park pooling station) | 14 Termination details for HV & LV Kindly provide Termination details for HV & LV of the Transformers | Technical | Please refer S. No. 4 of Amendment
15 |  |  | General points | CEA(Solar park pooling station) | PAINTING PROCEDURE - Zinc chromate primer (two coats) Zinc chromate banned in India. However Zinc phosphate will be provided for paint procedure. | Technical | Accepted. Please refer S. No. 6 of Amendment.
16 | Section I | 2 of 13 | Title | ENGINEERING, DESIGN, MANUFACTURING, TESTING, AND SUPPLY INCLUDING PACKING, FORWARDING, TRANSPORTATION, FREIGHT, INSURANCE TILL SITE, UNLOADING AND STACKING AT SITE STORES, INSTALLATION, TESTING AND COMMISSIONING OF 5 NOS. 160 MVA, 220/33-33 KV POWER TRANSFORMERS FOR RADHA NESDA, GUJARAT” | Stacking at site store means "Whether all transformers shall be instructed to dispatch when the plinth is ready or will there be a storage at site. If so what will be the time frame between storage and installation commencement | Contractual | Kindly refer Amendment 01 sheet.
17 | Section I | 2 of 13 | Title |  | All 5 Transformers shall be installed at Radha Nesda. Please confirm | Contractual | The understanding is correct.
18 | Section II | 7 of 51 | 5.3 | The Tender Processing Fee and EMD, if applicable is exempted for MSE Vendors registered under NSIC/ Udyog Aadhaar/DIC Category only. | We are registered under MSME/Udyam. Hope the EMD & Tender processing fee is exempted for us. Please confirm | Contractual | The Bid Processing Fees and EMD are exempted for eligible bidders who are registered MSEs under NSIC/ DIC/ Udyog Aadhaar Category only. As per Ministry of MSMEs (MoMSME) Gazette notification No. S.O. 4926(E) dated 18.10.2022 bidders will be eligible to avail all non-tax benefits of the category (micro or small or medium) it was in before the re-classification, for a period of three years from date of such upward change. In case the bidder proposes to meet the qualifying requirements based on the credentials of its Parent /Holding /Subsidiary /Affiliate and any of its Parent /Holding /Subsidiary /Affiliate is not an MSE, the bidder will not be eligible for exemption of Bid Processing Fees and EMD.
19 | Section II | 9 of 51 | 10.I | Further, Bidder shall submit the above-mentioned Fundamental Bid Compliance documents only under Offline Mode, which are required to establish the Fundamental requirements of the Bids. Same are required to be submitted to SECI Office, maximum within “Last Date & time of online Bid submission + 2 Working Days” | So the last date for offline BID compliance documents shall be by 25.01.2026 please confirm | Contractual | Two additional working days are provided solely for the submission of the Fundamental Compliance Document, as specified in the ITB section of the tender document. However, all documents must be dated prior to the last date of online bid submission. The extra days are granted only to accommodate delays in the submission of hard copies due to courier-related issues or similar reasons.
20 | Section V | 2 of 9 | 3.1 | Issue of Purchase Order or Notice to Proceed (NTP), whichever is later | whether NTP will be given for all quantities at a time? | Contractual | NTP (if provided) will be for the complete supply.
21 | Section V | 7 of 9 | 13 A . i | Supply portion shall be released to supplier upon receipt of unconditional acceptance of CA, detailed Performa invoice of contractor and against submission of unconditional & irrevocable Advance Bank Guarantee (ABG) with a validity period up to date of final supply amounting to 110% of total advance amount. The ABG needs to be submitted in addition to the Contract Performance Security and as per the Format -16 supplied in the Sample Forms and Format section of the tender document. | Anticipated validity for ABG shall be 16 Months from NTP. Please confirm | Contractual | Yes, the understanding is correct.
22 | Section V | 8 of 9 | 13 A . ii | Eighty percent (80%) of the total value of Supply portion shall be paid upon dispatch of transformers (along with mandatory spares and other equipment's) from manufacturer's works on pro rata basis on production of invoices and satisfactory evidence of shipment which shall be original Goods Receipt or receipted GR/Rail Receipt including Material Dispatch Clearance Certificate (MDCC) issued by the Owner’s Corporate QA & I representative and copy of Insurance for the supplied goods issued by the Supplier. | Upon dispatch of transformers means On production of invoice, Lorry Receipt, MDCC issued by Owners QA . please confirm Whether MDCC will be issued for spares of each qty along with transformer Prorata means what will be the disbursing proportion and the maximum period for releasing complete payment | Contractual | Dispatch of Transformers means dispatch from manufacturers site. Yes, MDCC must be submitted for spares also. The payment will be released as per the Payment Terms on the basis of detailed Delivery Schedule to be formulated post award of the Contract with the L1 Supplier. Payment shall be released within 30 days of submission and acceptance of invoice by the Engineer In Charge.
23 | Section V | 8 of 9 | 13 A . Iii | Ten percent (10%) payments of the total value of Supply portion shall be paid on Pro rata basis against supply, receipt and acceptance of Materials at site on submission of documents (except Advance Bank Guarantee) indicated under clause i) above, Contractor’s detailed invoice & packing list identifying contents of each shipment, evidence of dispatch (GR/ LR copy), Manufacturer’s/ Contractor’s Guarantee certificate of Quality and MDCC (Material Dispatch Clearance Certificate) issued by Owner’s authorized representative in original and Material Receipt Note (MRN). | What will be the Cap for MRN date from the date of delivery at site | Contractual | Payment shall be released within 30 days of submission and acceptance of invoice by the Engineer In Charge.
24 | Annexure to BDS | 5 of 11 | iv | In case the Supplier does not have type tests for the Supply Items under the RfS, Bidder shall submit an undertaking to the effect that the Type Tests shall be submitted prior to Supply. | Please confirm the applicability of short circuit test under type tests | Technical | Please refer Clause 1.7.3 of Technical Specifications.
25 | Section VIII | 8 of 18 | 1.7.3 | Short Circuit Test In case short circuit test has not been conducted or the test report not meeting the specification requirement for the offered transformer manufacturer, Bidder /Sub vendor shall establish” Ability to withstand the dynamic effects of short circuit ”for the offered transformer as per latest IEC 60076-5.The ability to withstand the dynamic effects of short circuit can be established either by (i) performing actual short circuit test or (ii) by method of calculation with reference to short circuit tested reference transformer as per IEC-60076-5/Annexure-A&B, in case short circuit test has been done on a similar transformer. | As per IEC 60076-5 the ability to withstand the dynamic effects of short circuit shall be demonstrated either – by tests, or – by calculation and design and manufacture considerations. So method of calculation shall be considered irrespective of performing test on similar rating. Please confirm the same When a short-circuit test is selected, it shall be regarded as a special test (see 3.11.3 of IEC 60076-1) and under type tests. | Technical | For the requirement of Dynamic Short Circuit Test, please refer Clause 1.7.3 of Technical Specifications. Please refer S. No. 7 of Amendment
26 | Section II | 42 of 51 | 4.1.6 | Download Official Copy of Tender Documents from ETS Note: Official copy of Tender Documents is distinct from downloading ‘Free Copy of Tender Documents’. To participate in a tender, it is mandatory to procure official copy of Tender Documents for that tender. | In ETS portal no free copy of tender documents is available. It is necessary to pay tender processing fee to download the copies. But as per Section 3 Page no 2 of 12 Clause no 4 Tender processing fee is exempted for MSE vendors. Is it mandatory to download or can we use copies downloaded from owners website. if mandatory how to avail exemption in paying processing fee | Contractual | The tender copy are available to download from SECI's website and ETS Portal free of cost. The tender processing is necessary for bidder's participation. However, the Bid Processing Fees and EMD are exempted for eligible bidders who are registered MSEs under NSIC/ DIC/ Udyog Aadhaar Category only. As per Ministry of MSMEs (MoMSME) Gazette notification No. S.O. 4926(E) dated 18.10.2022 bidders will be eligible to avail all non-tax benefits of the category (micro or small or medium) it was in before the re-classification, for a period of three years from date of such upward change. In case the bidder proposes to meet the qualifying requirements based on the credentials of its Parent /Holding /Subsidiary /Affiliate and any of its Parent /Holding /Subsidiary /Affiliate is not an MSE, the bidder will not be eligible for exemption of Bid Processing Fees and EMD.
27 | ITB | Page 12 of 51 | 11.5 | Prices quoted by the Bidder, shall remain FIRM and Fixed and valid until completion of the Contract and will not be subject to variation on any account. | Please amend price basis from Firm to IEEMA PVC with PV base month of December-2025 | Contractual | Kindly refer Amendment 01 sheet.
28 | SPECIAL PURCHASE CONDITIONS (SPC) | Page 2 of 9 | GPC clause 1 | The total timeline for Completion for the entire 5 * 160 MVA, 220/33-33 kV PT Package in total shall be 16 (Sixteen) Months from the Date of the Purchase Order/Contract Agreement or Notice to Proceed (NTP), whichever is later. | Please amend completion period as below: The total timeline for Completion for the entire 5 * 160 MVA, 220/33 33 kV PT Package in total shall be 22-24 (Twenty Two- Twenty Four) Months from the Date of the Purchase Order/Contract Agreement or Notice to Proceed (NTP), whichever is later. | Technical | Delivery Schedule shall be as follows: Delivery of 1st Unit: 14 months from the Date of PO and balance quantity till 16 months
29 | Sub-Section B: TS-Electrical | Page 8 of 18 | 1.7.3 | Short Circuit Test In case short circuit test has not been conducted or the test report not meeting the specification requirement for the offered transformer manufacturer, Bidder /Subvendor shall establish” Ability to withstand the dynamic effects of short circuit ”for the offered transformer as per latest IEC 60076-5.The ability to withstand the dynamic effects of short circuit can be established either by (i) performing actual short circuit test or (ii) by method of calculation with reference to short circuit tested reference transformer as per IEC-60076-5/Annexure-A&B, in case short circuit test has been done on a similar transformer. | Our T1 manufacturing plant at Kanjurmarg, Mumbai is closed now and we have shifted the manufacturing facilities from T1 plant, Mumbai to T3 plant at Mandideep. Currently, we are executing all orders from our T3 plant at Mandideep, M.P. In view of above, please confirm that Short Circuit Test Report on Transformers done by same manufacturer but from their different plant is acceptable to SECI. | Technical | Accepted
30 | ANNEXURE TO BDS | Page 3 of 11 | iii. of 1.2 | iii. The bidder must have supplied 220 kV class or above Power Transformers anywhere in India during the past 3 (three) years. Bidder shall submit any of the following: • Copies of relevant Purchase Orders and • Material Delivery Clearance Certificate, or • Delivery Completion Certificate, or • Invoice Copies. | Against this QR supporting document, we can submit Copies of relevant Purchase Orders and Invoices Copies only and not Material Delivery Clearance Certificate and Delivery Completion Certificate. In view of same please confirm that bid shall be acceptable to SECI. | Technical | Terms and conditions of the tender shall prevail
31 |  |  |  | PERFORMANCE BANK GUARANTEE | Please amend PBG from 10% to 3%. | Contractual | The terms and conditions of the tender document shall prevail.
32 | Bid Information Sheet | 12 of 240 | (F) | Completion: 16 Months | In view of long lead items involved in said 160 MVA, 220/33-33 kV Rating Transformer; we request to change the completion time from 16 months to 24 months. | Contractual | The terms and conditions of the tender document shall prevail.
33 | BID DATA SHEETS (BDS) | 70 of 240 | BID VALIDITY (ITB 14.1) | The bid validity period shall be 180 (One Hundred and Eighty Days) from the date of opening of Techno-Commercial Bid (Envelope-I). | In view of volatile trend in major commodities involved in transformer manufacturing, we request to change the bid validity period from 180 Days to 90 Days from the date of opening of Techno-Commercial Bid (Envelope-I). | Contractual
34 | SECTION - IV: GENERAL PURCHASE CONDITIONS (GPC) | 123 of 240 | 53.2; Defects Liability Period | Defects Liability Period: 12 (Twelve) Months Period of Liability from the date of material delivery at site. | Applicability of Defects Liability Period (DLP) will be on the pro-rata basis i.e. DLP will be reckoned from the date of supply of individual transformer. | Contractual | Yes, the DLP will be dealth according to the detailed clause as mentioned in the tender document.
35 | SECTION - IV: GENERAL PURCHASE CONDITIONS (GPC) | 124 of 240 | 53.2.10 | Defects Liability Period: Upon correction of the defects in the Facilities or any part thereof by repair/replacement, such repair/replacement shall have the defect liability period of twelve (12) months from such replacement. | Defects Liability Period (DLP) of such repaired and / or replaced parts will not exceed the original Defects Liability Period (DLP) of the main equipment i.e. transformer. | Contractual | The terms and conditions of the tender document shall prevail.
36 | SECTION - IV: GENERAL PURCHASE CONDITIONS (GPC) | 132 of 240 | 70. | Transit / Cargo Insurance: Amount -> 110% of the Ex-works value of supply. | Amount of Transit / Cargo Insurance to be changed to 100% of the Ex-works value of supply. | Contractual | The terms and conditions of the tender document shall prevail.
37 | SECTION - II: INSTRUCTION TO BIDDERS (ITB) | 27 of 240 | 11; 11.5 | SCHEDULE OF RATES (SOR)/ PRICE SCHEDULE (PS)/ BID PRICES: Prices quoted by the Bidder, shall remain FIRM and Fixed and valid until completion of the Contract and will not be subject to variation on any account. | In view of volatile trend in major commodities involved in transformer manufacturing & long completion period, we request to change the price basis from Firm to Variable subject to IEEMA's Latest PV (Price Variation) Formula w.e.f. 1st Sept. 2021 with the Base Date as "One Month Prior to the Date of Tendering"; & Without any ceiling on either side. | Contractual | Kindly refer Amendment 01 sheet.
38 | SECTION - V: SPECIAL PURCHASE CONDITIONS (SPC) | 137 of 240 | 3. | The total timeline for Completion for the entire 5 * 160 MVA, 220/33-33 kV PT Package in total shall be 16 (Sixteen) Months from the Date of the Purchase Order/Contract Agreement or Notice to Proceed (NTP), whichever is later. | In view of long lead items involved in said 160 MVA, 220/33-33 kV Rating Transformer; we request to change the completion time from 16 months to 24 months from the Date of the Purchase Order / Contract Agreement or Notice to Proceed (NTP), whichever is later. | Contractual | The terms and conditions of the tender document shall prevail.
39 | SECTION - V: SPECIAL PURCHASE CONDITIONS (SPC) | 139 of 240 | 6; Contract Performance Security (GPC clause 25); 25.7 | Further, any delay beyond 30 (Thirty) days in the submission of performance security shall attract interest @ 1.25% per month on the total Contract Performance Security amount, calculated on pro-rata basis accordingly. Owner at its sole discretion may cancel the Contract & forfeit 100% of EMD if applicable in case Contract Performance Security is not submitted within 45 (Forty-five) days from issuance of Contract. | We confirm to submit the Performance Security within 30 (Thirty) days from date of issuance of Contract. However, request you to withdraw the interest condition; & also withdraw the condition of EMD forfeit. | Contractual | The terms and conditions of the tender document shall prevail.
40 | SECTION - V: SPECIAL PURCHASE CONDITIONS (SPC) | 142 of 240 | 13; Schedule of Rates & Payments (GPC clause 78) | Interest free advance (optional) of 10% of the total value of Supply portion shall be released to supplier upon receipt of unconditional acceptance of CA, detailed Performa invoice of contractor and against submission of unconditional & irrevocable Advance Bank Guarantee (ABG) with a validity period up to date of final supply amounting to 110% of total advance amount. | Value of ABG to be changed from 110% of total advance amount to 100% of total advance amount. | Contractual | The terms and conditions of the tender document shall prevail.
41 | SECTION - II; INSTRUCTION TO BIDDERS (ITB) | 40 of 240 | 31; EVALUATION OF BIDS & E REVERSE AUCTION 31.4 | EVALUATION CRITERIA; (ii) Engineering, design, testing, packing, forwarding, transportation, freight, insurance till site, unloading, stacking at site stores, installation, testing and commissioning and Other Services including GST/Taxation as per Schedule No 2/SOR 2. | We request to remove the activity "stacking at site stores" from the scope of work of the Bidder. | Contractual | Kindly refer Amendment 01 sheet.
42 |  |  | Cl. No, 1 | The Power Transformer specification, rating, configuration, dimension and foundation design shall be as per “Standard Technical Specifications of Transformer(s) for solar park Pooling Station” issued by CEA | 1. Kindly note that, we do not have similar S.C tested unit to meet criteria for similar transformer is specified in Annexure-J of CEA standard spec. Similarity comparison with deviation enclosed for your review and acceptance. 2. Dynamic short circuit test not envisaged on offered transformer. 3. Further we can provide S.C test certificates of higher rating transformers. Kindly confirm if the same is acceptable. | Technical | In case of non availability of Dynamic Short Circuit Withstand Test for the proposed equipment, the Bidder shall establish similarity as per Criteria for Selection of Similar Reference Transformer for Dynamic Short Circuit Withstand Test prescribed in Annexure J of the CEA Specifications for Solar Park
43 |  |  | Cl. No, 1.2 | Insulation Levels | In the absence of insulation levels we propose to offer insulation as per CEA recommendations i.e., HV 19.1 Lighting Impulse Voltage 950kVp 19.3 One minute Power frequency withstand capability (kV rms) 395. Please accept. | Technical | Accepted
44 |  |  | Cl. No. 1.3 | no inhibitors shall be used in oil | Kindly note that, spec requirement(uninhibited) & CEA std spec Annexure-L(Inhibited) are contradictory. Please confirm which one to follow.. | Technical | Unused inhibited Oil (Type A, High Grade) as per IS 335/IEC 60296 shall be used as per CEA Specifications. Please refer S. No. 8 of Amendment.
45 |  |  |  | The Bidder shall ensure that windings of all transformers are made in clean, dust proof (Cleanroom class ISO 9 or better as per ISO 14644-1), humidity controlled environment with positive atmospheric pressure. The bidder shall furnish details of the facilities available at his works along with the bid. | Bidder shall ensure that winding for Transformer are made in clean, dust proof (Cleanroom class ISO 9 or better as per ISO 14644-1) environment. | Technical | Noted.
46 |  |  |  | Termination | In the absence of terminal details we understand that, termination is with oil-to-air bushings for all bushings. Please confirm. | Technical | Please refer S. No. 4 of Amendment
47 |  |  |  | Site | Please let us know site dimensional limitation if any. Kindly provide clear site layout drawings with dimensions. | Technical | No dimensional limitation for the site.
48 |  |  |  | SERVICE CONDITION | In the absence of site details we are considering below, Site altitude <1000m Maximum ambient temperature 50DegC Yearly weighted average cooling air ambient temperature: 32 Deg.C Seismic zone and ground acceleration (both in horizontal & vertical direction): Zone-II (0.1g) as per IS 1893 Coastal considerations(Yes/No): No Please confirm | Technical | Location: Radha Nesda, District Banaskantha, Gujarat Latitude & Longitude: 24.507°N, 71.281°E Site altitude <1000m Maximum ambient temperature: 50°C Seismic zone: Zone-IV as per IS 1893 Coastal considerations: Yes (C5)
49 |  |  |  | Spares, Commissioning & start-up spares list | We have not consider commissioning spare, O&M spares, Testing and maintenance equipment and special tools-tackles which are not required. Please let us know in case of any specific mandatory spare requirement. | Technical | Testing and Commissioning not in the scope of the Supplier. However, Supplier shall depute a representative to provide supervision of erection, testing and commissioning as per Clause 3.3 of Scope of Works.
50 |  |  | Chapter-2 clause 13.0 | A minimum of 5% of the oil quantity shall be supplied as spare (in addition to first filling) | We confirm to provide spare oil as specificied in Annexure-I BoQ spares Only. We understand that, which already includes 5% spare oil mentioned in CEA. | Technical | Accepted
51 |  |  |  | Manufacturing Quality Plan (MQP) Below is CEA standard requirement: "…......The Quality Plan shall be submitted to purchaser, for review and approval. Typical Manufacturing Quality Plan (MQP) is provided at Annexure-E for reference. Any change in practice or acceptance norms (with reference to various tests / parameters in respective National / International standard) would be suitably incorporated by manufacturer from time to time and submit the same for approval of purchaser / utility." | Note that Quality plan provided in CEA is typical MQP for reference purpose only. We propose to offer Hitachi Energy standard MQP as per best industry standards for subject enquiry as suggested in CEA. The same will be submitted during detailed engineering. | Technical | Noted.
52 |  |  |  | Each digital RTCC relay shall be used to control one unit of transformer. No. of relays including spare relay, if any, shall be specified by the utility as per requirement. | Please confirm number of digital relays per panel required for this project. | Technical | As per the bidder’s proposed design to meet the tender-stipulated functions of the RTCC panel.
53 |  |  |  | Annexure-N/P 3. l) In case of transformers with separately mounted cooler / radiator bank, the position of the cooler / radiator bank has been recommended on the left side of the transformer when viewing from HV side. However, transformer shall be designed in such a way that cooler / radiator bank can be positioned on either side of the main tank. Similarly the conservator shall be on the left side of the tank while viewing from HV side. | We propose to offer separately mounted cooler bank placed on left side of the tank watching from HV side of the transformer. Please let us know the any space constraints at site to check feasibility for Provision to provide cooler bank either side of the tank. | Technical | No space constraint
54 |  |  |  |  | We are registered under MSME as a Medium Enterprise. We kindly request exemption from submission of Earnest Money Deposit (EMD). We shall submit an undertaking on our company’s letterhead towards Bid Security, if required. | Contractual | The terms and conditions of the tender document shall prevail.
55 |  |  |  |  | We request you to kindly amend the price schedule to allow price on a variable basis, linked to IEEMA Base Date of December 2025, to account for fluctuations in raw material prices. | Contractual | Kindly refer Amendment 01 sheet.
56 |  |  |  |  | We request clarification and amendment that the scope of work be limited up to supply of transformers only. Arrangement of unloading at site may kindly be kept in the Buyer’s scope, as the Buyer is better placed to manage site-specific conditions and availability of suitable handling facilities. | Contractual | Kindly refer Amendment 01 sheet.
57 |  |  |  |  | Also please share GTP format (if any) along with a list of GA Drawings required during the bidding stage. | Technical | GA and GTP are not required during bidding stage. Same shall be submitted during detailed engineering as per CEA standard's Annexure A

## Amendment-1
Tender for Turnkey Supply Package for 5 nos. of 160 MVA, 220/33-33 kV Power Transformer at Radha Nesda, Gujarat, India
Tender No : SECI/C&P/OP/11/022/2025-26
S. No. | Section | Page No. | Clause | Original Version | Amendment
1 | - | - | - | General Clarification | The bidder scope only includes ENGINEERING, DESIGN, MANUFACTURING, TESTING, AND SUPPLY INCLUDING PACKING, FORWARDING, TRANSPORTATION, FREIGHT, INSURANCE TILL SITE OF 5 NOS. 160 MVA, 220/33-33 KV POWER TRANSFORMERS. The UNLOADING AND STACKING AT SITE STORES, INSTALLATION, TESTING AND COMMISSIONING OF 5 NOS. 160 MVA, 220/33-33 KV POWER TRANSFORMERS is not under bidder's scope.
2 | - | - | - | Tender Title: Tender for ENGINEERING, DESIGN, MANUFACTURING, TESTING, AND SUPPLY INCLUDING PACKING, FORWARDING, TRANSPORTATION, FREIGHT, INSURANCE TILL SITE, UNLOADING AND STACKING AT SITE STORES, INSTALLATION, TESTING AND COMMISSIONING OF 5 NOS. 160 MVA, 220/33-33 KV POWER TRANSFORMERS FOR RADHA NESDA, GUJARAT | Tender Title: Tender for ENGINEERING, DESIGN, MANUFACTURING, TESTING, AND SUPPLY INCLUDING PACKING, FORWARDING, TRANSPORTATION, FREIGHT, INSURANCE TILL SITE OF 5 NOS. 160 MVA, 220/33-33 KV POWER TRANSFORMERS FOR RADHA NESDA, GUJARAT
3 | Section V Special Purchase Conditions (SPC) | 144 | 16 | Additional Clause related to Price Variation | Price Variation (PV) Clause and Basis: a. Offered Price shall be based on latest IEEMA -published Price Variation (PV) formula for Power Transformers of voltage above 33 kV and up to 400 kV supplied against domestic contracts (as on the last date of Bid Submission). b. This formula would attract an upper Price variation ceiling of 15% (Fifteen Percent), beyond which no price variation would be provided. c. Further, no price variation would be provided to the Transformer supplier till any price variation upto 5% (Five Percent) price change. d. IEEMA Price Variation shall be calculated on 100% Ex-works price of transformer (as quoted by Bidder in Financial Proposal, Schedule of Rates 1). e. For the purpose of Price Variation calculation: I. The Contract Price emerged post applying the above-mentioned Price variation clause in the Contract Price of the successful bidder will be determined as the final Contract Price & accordingly the related contractual obligations will be accordingly calculated based on such final Contract price, Ex Liquidated damages, Advance availed and its adjustments (If applicable), Performance Security etc. Such correction in the final Contract Value of the Transformer Contract may so happen mid-course or during the Final Closure of the project, based on the arrival of the final dates of determination of such PV Clause. II. The Price Variation formula shall be restricted to supply part of the Transformer only, as per Schedule of Rates 1 of the Financial Bid, excluding GST. GST shall be charged on the adjusted price after applying PV. III. Base date for the purpose of price variation to be considered: Last date of Bid Submission deadline. IV. Final date for the purpose of price variation to be considered: Earlier of the following: 1. Date on which the transformer is notified as ready for inspection by the Supplier. 2. Scheduled Delivery Date: 14 months from the date of Award plus Extension provided by the Owner. Note: No upward price variation will be admissible beyond this scheduled delivery date for defaults on the part of the supplier. However, a downward price variation would be availed by the Employer as per the letter of extension of the delivery period.
4 | Section VII Technical Specifications (TS) | 222 | 1.2 | Termination HV side: Outdoor LV side: Outdoor HVN/LVN: Outdoor | Termination: HV: Outdoor, Oil-to-Air Bushing LV: Cable Box with Disconnecting Chamber HV-N: Outdoor, Oil-to-Air Bushing LV-N: Outdoor, Oil-to-Air Bushing
5 | Section VII Technical Specifications (TS) | 222 | 1.2 | Cooling Fans shall be of minimum IP66 protection. | Cooling Fans shall be of minimum IP65 protection.
6 | Section VII Technical Specifications (TS) | 223 | 1.5 | Painting - Shall be suitable for C-5 environment as per ISO 12944-5:2019. | Painting - Shall be suitable for C-5 environment as per ISO 12944-5:2019. Accessories and valves manufactured from inherently corrosion-resistant materials (e.g., gunmetal/bronze) need not be included in the C5 painting system. However, any other exposed surfaces that are vulnerable to corrosion shall meet the specified environmental durability requirements. In addition to Zinc Chromate mentioned in CEA standard, Zinc-rich primers like Zinc Phosphate (IS 2932:2025) are also admissible for components like cast iron valves and RTCC panels.
7 | Section VII Technical Specifications (TS) | 228 | 1.7.4.2 | Type Tests …. 2. Short circuit Test as per IEC 60076-5 (if applicable) …... | Type Tests/Special Tests ….. 2. Short circuit Test as per IEC 60076-5 (Please refer Clause 1.7.3 above) …...
8 | Section VII Technical Specifications (TS) | 222 | 1.3 | Insulating Oil No inhibitors shall be used in the transformer oil......... | Insulating Oil The insulating oil shall be unused inhibited (Type A, High Grade) Transformer Oil conforming to IS 335/IEC-60296-2020.........